| DEPARTMENT OF HEALTH SERVICES Division of Public Health F-01573 (06/2015) | STATE OF WISCONSIN Bureau of Environmental and Occupational Health DHS.WISCONSIN.GOV Page 1 of 2 |
| --- | --- |
| LOG OF ICE ARENA AIR QUALITY |  |
| Pollution levels can fluctuate, so a one-hour time-weighted average is used to assess whether or not contaminant levels are too high. To calculate a time-weighted average, stand inside the rink on the centerline. Hold the monitor at board height and follow these three simple steps: |  |

| Record the air quality measurement every five minutes for an hour, starting at zero minutes and ending at 60 minutes. |  |  | Add together the 13 measurements taken. Divide this number by 13 (the total number of measurements taken). |  |  |  | This number is your time-weighted average. Ensure the levels do not require action (see below). |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Recommended Frequency of Air Quality Tests If the rink uses . . . - Gas powered resurfacer: at least twice every 7 days (do one test on the weekend and one test on the next busiest day) - Gas powered edger: at least once every 7 days - Other gas powered equipment: If open for business, test every 15 minutes while equipment is in use; if not open, test prior to opening the next day |  |  |  |  |  |  |  |  |  |
| When to Take Action |  |  |  |  |  |  |  |  |  |
| Corrective Action |  | 25 ppm for CO 0.30 ppm for NO2 |  |  | Immediately Evacuate |  | 125 ppm for CO 2.00 ppm for NO2 |  |  |
| Immediately increase ventilation and stop the use of gas-powered equipment. |  |  |  |  | Remove all people from the facility and into fresh air immediately. |  |  |  |  |

Log on page 2

| F-01573 (06/2015) Log of Ice Arena Air Quality | Page 2 of 2 |
| --- | --- |

| Date | Time AM / PM | Number of Previous Resurfaces Today | Carbon Monoxide Level | Nitrogen Dioxide Level | Comments | Print Name of Person Conducting Test |
| --- | --- | --- | --- | --- | --- | --- |